## HEATONLY
HEATING LOAD CALCULATIONS
Building Name Here
DESIGN CONDITIONS
| Winter Outdoor Design dry bulb |  |  | 19 | Deg. F
Building Elements
Walls
|  | CMU Wall |  | R Value
|  | Inside Surface |  | 0.61
|  | Gypsum Drywall, 1/2" |  | 0.045
|  | 4" Fiberglass Insulation |  | 11
|  | 8" Conc. Blocks |  | 1.04
|  | Outside Surface |  | 0.017
|  |  | Total R | 12.712
Roof
|  | Metal with rigid Insulation |  | R Value
|  | Inside Surface |  | 0.61
|  | Metal decking |  | 0.001
|  | 4" Rigid Insulation |  | 20
|  | Outside Surface |  | 0.017
|  |  | Total R | 20.628
GLASS
|  | U-value |  | 0.49
ZONE LOAD CALCULATIONS
| Zone Name: | Entire Building
| Length = | 100 | FT
| Width = | 150 | FT | Room Temperature
| Height = | 20 | FT | Heating | 70 | Deg. F
Heating Loads (Neglecting internal gains)
|  | U-Value | Net Area | TD | BTU/Hr
| Roof | 0.048478 | 15000 | 51 | 37085.5148
| Wall 1 | 0.078666 | 2000 | 51 | 8023.9144
| Wall 2 | 0.078666 | 3000 | 51 | 12035.8716
| Wall 3 | 0.078666 | 2000 | 51 | 8023.9144
| Wall 4 | 0.078666 | 3000 | 51 | 12035.8716
| Glass | 0.49 | 1436 | 51 | 35885.64
|  | CFM | AC/hr
| Infiltration | 2500 | 0.5 | 51 | 137700
|  |  | 0.16667 | CFM/SF
Total Heating Load |  |  |  |  | 250790.7269 | BTU/hr